Lincoln Amphitheatre HVLS Ceiling Fan Project

Scope of Work

- Contractor to disconnect existing ceiling fans and controllers and abandon fans and wiring in place.

- Contractor to provide and install (2) – Rite-Hite Revolution Series, high-volume, low-speed fans outdoor rated, and have a minimum diameter of 24’-0”. Additional specifications below. Fans are to be located BELOW the wiring mesh and mounted to the steel structure of the Amphitheatre.

- Contractor to have a licensed engineer verify all proposed fan supports and existing structural members are structurally capable of supporting the new fans and their components at the proposed mounting locations.

- Provide and install a 100A, 120/208V, 3ph, 4w, 30 circuit panel in Mechanical Room 203 on the 2nd floor sound booth to allow for 3-phase power to ceiling fans. Panel to be fed from 100A, 3 pole breaker installed in Panel G in the Mechanical Room 203 on the 2nd floor of the sound booth. Rearrange breakers in existing Panel G as necessary to install new sub-panel.

- Contractor provide 208-240V, 3-phase power to fans from the new panel located in Mechanical Room 203 in the 2nd floor of the Sound Booth at rear of the Amphitheatre. All conduit to ceiling fans to be painted BLACK.

- Contractor to provide and install (1) – Rite-Hite Fan Commander 2.0 Controller in Mechanical Room 203.

- Fan installation to include all 3 phase power, control wiring, lift rental, and bird screen repair required to install the fans. Fan specifications are listed below.

Fan Specifications:

| Fan Diameter: | 24’ Diameter | Motor Shroud: | Yes |
| --- | --- | --- | --- |
| Mounting Option: | I-Beam Bracket | Custom Paint: | Standard Mill Finish |
| Drop Tube Assembly | Yes | Controls | Fan Commander Controls by Rite-Hite |
| Voltage/Phase: | 208-240V, 3 phase |  |  |
| Low Headroom Blades: | No |  |  |

Drawings of Fan Locations and also of the new sub-panel location are attached.

Each fan weight is approximately 250 pounds.